## Calculator - Home
Required Tabulated Current Capacity of cable (It) | 61.5385 | B3/(B5*B6*B7*B8)
OPD Rating (Select) | 32
Ambient Temperature factor | 1 | Factor = 1.00 for 30c
Grouping Factor | 0.52 | Factor = 0.52 (8 cables, 2 excluded due to < 30% tabulated load )
Thermal Insulation Factor | 1 | Factor = 1 due to Insulation as defined per tables F4, F5, F6
OPD is not a BS 3036 Fuse | 1
0.3 * Gg (0.45 for 10 cables) * It (Colum D)
Circuit | MCB Rating (A) | Notes | Initial Tabulated Grouped Rating in Amps | 30% of initial grouped Rating in Amps | Expected amps with Diversity | Excluded due to <30% load | Corrected group rating in Amps (N minus M)(0.52)
Induction Hob (6mm) | 32 |  | 71 | 9.585 | 16.6 | No | 61.53
Kitchen Radial Sockets (4mm) | 32 |  | 71 | 9.585 | 32 | No | 61.53
Electric Oven (2.5mm) | 20 |  | 44 | 5.94 | 15.4 | No | 38.46
Downstairs Radial Sockets (2.5mm) | 20 |  | 44 | 5.94 | 8 | No | 38.46
Upstairs Radial Sockets (2.5mm) | 20 |  | 44 | 5.94 | 8 | No | 38.46
Old Radial Sockets (2.5mm) | 16 |  | 35 | 4.725 | 6.4 | No | 30.76
Downstairs Lights (1.5mm) | 6 | Diversity based before LED's | 13 | 1.755 | 3.47 | No | 11
Upstairs Lights (1.5mm) | 6 | Diversity based before LED's | 13 | 1.755 | 1 | Yes | 11
Old Lights (1.5mm) | 6 | Diversity based before LED's | 13 | 1.755 | 1.9 | No | 11
Smoke Alarms (1.5mm) | 6 | Negligible Load | 13 | 1.755 | 0.1 | Yes | 11
OCP rating
3
6
10
16
20
25
32
40
45
50
63
100